## Cooler
Basic Display | KE2 Combo Display | Walgreen's | Description
Usename: | Hussmann
tS | Room Temp | 35.0 F | Room Temperature to be maintained
rFG | Refrigerant | R-448A | Refrigerant used
dtY | Defrost Type | Air | (ELE) for Electric. (Air) for off time. (HGn) for hot gas with LLS relay on. (HGF) for hot gas with LLS relay off.
Edt | Valve Type | SER-AA to L. | Expansion valve used on system.
ind | Defrost Mode | Demand | Mode to initiate defrost. (dnd) demand. (SCH) schedule. (rnt) comp run time.
dPd | Defrost / Day | 5 | If Defrost Mode=Sch: Defrost per day. Number of evenly spaced defrosts per day.
dtP | Defrost Term Temp | 37.0 F | Temperature the coil sensor(s) must exceed to terminate defrost.
dEF | Defrost Parameter | 40 | If Defrost Mode= Demand: Coefficient to KE2 Defrost algorithm
dtL | Max Defrost Time | 45 min | If Defrost Mode=Sch: Maximum amount of time the defrost relay will be energized
drn | Drain Time | 0 min | Time to be in drain mode (drip time).
rFt | Refrig Fan Type | Permanent | Select evaporator fan management. (CYC) cycle, ie. Manage, fans during refrigeration and off cycle. (FoC) fans on w/ compressor will primarily manage fans only during the off cycle. (PEr) permanent forces the fans to run during refrigeration and off cycle. (t24) Title 24 cycles fans based on Title 24 regulations.
FtS | Min Fan Switch Time | 10 sec | Minimum time before fans can be turned on again after turning off.
Stt | Superheat | 8.0 F | Target superheat value. Only applies when non-mechanical valve selected. When mechanical valve is selected it is the high superheat alarm threshold.
LPt | Low Pressure Cut Out Time | 0 min | If EEV selected: Advanced topic, 0=Disabled
LPC | Low Pressure Cut Out | 8.0 psig | If LPt greater then 0: Advanced topic.
LPd | Press Diff for LPCO | 15.0 psig | If LPt greater then 0: Advanced topic.
Att | LPCO Attempts | 5 | If LPt greater then 0: Advanced topic.
rnt | Comp Run Time | 6 hrs | If Defrost Mode- rnt: Hours of cooling before starting a defrost.
Htn | Electric Defrost Mode | Pulse | If Defrost Type= ELE: (Prn) Permanent, leaves defrost relay energized during the defrost cycle. (PUL) Pulse, utilizes advanced heater management.
HAo | High Temp Alarm Offset | 10.0 F | Degrees above Room Temp+Air Temp Diff to trigger High Temp Alarm.
Had | High Temp Alarm Delay | 60 min | Delay before triggering a High Temp Alarm
LAo | Low Temp Alarm Offset | 4.0 F | Degrees below Room Temp to trigger Low Temp Alarm
LAd | Low Temp Alarm Delay | 10 min | Delay before triggering a Low Temp Alarm
dAd | Door Alarm Delay | 30 min | Time door must be open before triggering a Door Open Alarm. Requires door switch to activate
AU1 | Aux In 1 Mode | CLt | See Auxiliary Input Modes
A1A | Aux In 1 State | Closed | (oPn) active if input is open. (CLo) active if input is shorted
AU2 | Aux In 2 Mode | Disabled | See Auxiliary Input Modes
A2A | Aux In 2 State | Closed | (oPn) active if input is open. (CLo) active if input is shorted
AU3 | Aux In 3 Mode | Sys Off | See Auxiliary Input Modes
A3A | Aux In 3 State | Closed | (oPn) active if input is open. (CLo) active if input is shorted
tS2 | 2nd Room Temp | -50.0 F | If AU1, AU2, or AU3=(t2n) 2nd Room Temp: This value becomes the Room Temp set point when the Auxiliary Input is active
10t | 0 To 10 VDC Mode | Alarm Relay | (ALr) Alarm relay. (FSd) Evap Fan Speed Control. (dAL) Door alarm relay.
tEt | Multi Evap Mode | Off | Mode for Lead/Lag operation. (oFF) Off. (LGC) Redundant Cool. (LGF) Redundant Off. (ALt) Alternate.
PAd | Paired Defrost Mode | Off | Select operation when lead/lag pair controller goes into defrost. (oFF) Off. (AUt) Auto.
LLt | Lead/Lag Time | 12 hours | Time to toggle between lead/lag
Unt | Temp Units | Fahrenheit | Display temperature in F or C. (FAH) Fahrenheit. (CEL) Celsius.
EdF | Extreme Temp Diff | 20.0 F | Should not be adjusted unless instructed to by KE2 Therm
CLA | Clear Alarms | - | Press and hold ENTER until red LED starts blinking, alarms will be reset. Sensor and transducer alarms will immediately return until fixed.
diA | Diagnostics Mode | - | Press and hold Enter until FAr is displayed. Energizes each relay individually for 30 seconds: (FAr) fan relay, (dEr) defrost relay, (CPr) compressor relay.
FAC | Factory Reset |  | Press and hold Enter to reset the controller to the factory default set points
PAS | Web Password Reset |  | Press and hold Enter to reset the web password to the factory default.
PAr | Pair L/L | - | Press and hold Enter until red LED blinks. (PAS) successful pairing. (FAi) pairing failed. Only two controllers can be present on network.
UnP | Unpair L/L | - | Press and hold Enter until red LED blinks. (PAS) successful unpairing. (FAi) unpairing failed.
bnd | Bond | - | Press and hold Enter until red LED blinks. (PAS) successful bonding. (FAi) bonding failed. Only two controllers can be present on network.
Unb | Unbond | - | Press and hold Enter until red LED blinks. (PAS) successful unbonding. (FAi) unbonding failed.
SA | Smart Access | Disabled | Turn KE2 Smart Access on or off. (EnA) Enable KE2 Smart Access. (diS) Disable KE2 Smart Access.
dHC | DHCP | Enabled | Turn DHCP mode on or off. (EnA) Enable DHCP mode. (diS) Disable DHCP mode.
Not Available on Basic Display | Motor Type | Bipolar | Type of motor on electric valve used
| Motor Step Rate | 200 | Motor step rate for EEV
| Max Valve Steps | 2500 | Full stroke steps for EEV
| Max Operating Press | 150 psig | Max operating pressure. Mas is 300 when R-410a is selected and 500 when R-744 is selected
| Fan Speed | 0% | Fan Speed %
| Min Comp Run Time | 2 min | Minimum Compressor Run Time.
| Min Comp Off Time | 5 min | Minimum Compressor Off Time.
| 1st Defrost Delay | 120 min | Delay time for first defrost when using scheduled defrost.
| Defrost Fan State | Off(E) On(A) | Off=Fans off during defrost; On=Fan on during defrost
| Fan Delay Temp | 5.0 F | Fan delay temp after defrost only.
| Max Fan Delay Time | 3 min | Max fan delay time after defrost.
| Pump Down Time | 0 min | Minimum time between de-energizing the liquid line solenoid/compressor contactor relay and energizing the defrost relay.
| Multi Air Temp CTRL | Warmest | Warmest air=use the warmest air temp from bonded controls; Average air= use the average air temp from bonded controls.
| Multi Evap Cool | Synchronized | Synchronized=synchronize bonded controllers in refrigeration mode; Independent= bonded controllers control temperature independently.
| Multi Evap Defrost | Synchronized | Synchronized=synchronized bonded controllers in defrost mode; Independent=bonded controllers defrost independently.
| Multi Evap Sensor | Shared | Shared=share sensor readings from bonded controllers; Unshared=use local sensor readings only.
| Room Temp Ind Def | 0.0 F | Room temp while bonded controller is in defrost. Only applies to bonded controllers with Multi Evap Defrost set to Independent.
| Suct Pres Offset | 0.0 F | Offset added or subtracted from the suction line pressure transducer reading, if needed.
| Suct Temp Offset | 0.0 F | Offset added or subtracted from the suction temp sensor reading, if needed.
| Coil Temp Offset | 0.0 F | Offset added or subtracted from the coil temperature sensor reading, if needed.
| Air Temp Offset | 0.0 F | offset added or subtracted from the room temperature sensor reading, if needed.
| Aux 1 Offset | 0.0 F | When Aux1, Aux2, or Aux3 is used as a temperature sensor an offset is added or subtracted from the reading.
| Aux 2 Offset | 0.0 F
| Aux 3 Offset | 0.0 F
| Proportional | 3 | Coefficient to valve control algorithm that increases valve responsiveness as the value increases.
| Intergral | 5 | Coefficient to valve control algorithm that increases valve responsiveness as the value increases.
| Derivative | 3 | Should not be adjusted unless instructed to by KE2 Therm
| Air Temp Diff | 1.0 F | Degrees above Room Temp before the controller will begin refrigeration

## Freezer
Basic Display | KE2 Combo Display | Walgreen's | Description
tS | Room Temp | -10°F | Room Temperature to be maintained
rFG | Refrigerant | R-448A | Refrigerant used
dtY | Defrost Type | Electric | (ELE) for Electric. (Air) for off time. (HGn) for hot gas with LLS relay on. (HGF) for hot gas with LLS relay off.
Edt | Valve Type | SER-AA to L | Expansion valve used on system.
ind | Defrost Mode | Demand | Mode to initiate defrost. (dnd) demand. (SCH) schedule. (rnt) comp run time.
dPd | Defrost / Day | 5 | If Defrost Mode=Sch: Defrost per day. Number of evenly spaced defrosts per day.
dtP | Defrost Term Temp | 50.0 F | Temperature the coil sensor(s) must exceed to terminate defrost.
dEF | Defrost Parameter | 30 | If Defrost Mode= Demand: Coefficient to KE2 Defrost algorithm
dtL | Max Defrost Time | 45 min | If Defrost Mode=Sch: Maximum amount of time the defrost relay will be energized
drn | Drain Time | 2 min | Time to be in drain mode (drip time).
rFt | Refrig Fan Type | Permanent | Select evaporator fan management. (CYC) cycle, ie. Manage, fans during refrigeration and off cycle. (FoC) fans on w/ compressor will primarily manage fans only during the off cycle. (PEr) permanent forces the fans to run during refrigeration and off cycle. (t24) Title 24 cycles fans based on Title 24 regulations.
FtS | Min Fan Switch Time | 10 sec | Minimum time before fans can be turned on again after turning off.
Stt | Superheat | EEV=8.0 F | Target superheat value. Only applies when non-mechanical valve selected. When mechanical valve is selected it is the high superheat alarm threshold.
LPt | Low Pressure Cut Out Time | 0 min | If EEV selected: Advanced topic, 0=Disabled
LPC | Low Pressure Cut Out | 8.0 psig | If LPt greater then 0: Advanced topic.
LPd | Press Diff for LPCO | 15.0 psig | If LPt greater then 0: Advanced topic.
Att | LPCO Attempts | 5 | If LPt greater then 0: Advanced topic.
rnt | Comp Run Time | 6 hrs | If Defrost Mode- rnt: Hours of cooling before starting a defrost.
Htn | Electric Defrost Mode | Pulse | If Defrost Type= ELE: (Prn) Permanent, leaves defrost relay energized during the defrost cycle. (PUL) Pulse, utilizes advanced heater management.
HAo | High Temp Alarm Offset | 10.0 F | Degrees above Room Temp+Air Temp Diff to trigger High Temp Alarm.
Had | High Temp Alarm Delay | 60 min | Delay before triggering a High Temp Alarm
LAo | Low Temp Alarm Offset | 4.0 F | Degrees below Room Temp to trigger Low Temp Alarm
LAd | Low Temp Alarm Delay | 10 min | Delay before triggering a Low Temp Alarm
dAd | Door Alarm Delay | 30 min | Time door must be open before triggering a Door Open Alarm. Requires door switch to activate
AU1 | Aux In 1 Mode | CLt | See Auxiliary Input Modes
A1A | Aux In 1 State | Closed | (oPn) active if input is open. (CLo) active if input is shorted
AU2 | Aux In 2 Mode | Disabled | See Auxiliary Input Modes
A2A | Aux In 2 State | Closed | (oPn) active if input is open. (CLo) active if input is shorted
AU3 | Aux In 3 Mode | Sys Off | See Auxiliary Input Modes
A3A | Aux In 3 State | Closed | (oPn) active if input is open. (CLo) active if input is shorted
tS2 | 2nd Room Temp | -50.0 F | If AU1, AU2, or AU3=(t2n) 2nd Room Temp: This value becomes the Room Temp set point when the Auxiliary Input is active
10t | 0 To 10 VDC Mode | Alarm Relay | (ALr) Alarm relay. (FSd) Evap Fan Speed Control. (dAL) Door alarm relay.
tEt | Multi Evap Mode | Off | Mode for Lead/Lag operation. (oFF) Off. (LGC) Redundant Cool. (LGF) Redundant Off. (ALt) Alternate.
PAd | Paired Defrost Mode | Off | Select operation when lead/lag pair controller goes into defrost. (oFF) Off. (AUt) Auto.
LLt | Lead/Lag Time | 12 hours | Time to toggle between lead/lag
Unt | Temp Units | Fahrenheit | Display temperature in F or C. (FAH) Fahrenheit. (CEL) Celsius.
EdF | Extreme Temp Diff | 20.0 F | Should not be adjusted unless instructed to by KE2 Therm
CLA | Clear Alarms | - | Press and hold ENTER until red LED starts blinking, alarms will be reset. Sensor and transducer alarms will immediately return until fixed.
diA | Diagnostics Mode | - | Press and hold Enter until FAr is displayed. Energizes each relay individually for 30 seconds: (FAr) fan relay, (dEr) defrost relay, (CPr) compressor relay.
FAC | Factory Reset |  | Press and hold Enter to reset the controller to the factory default set points
PAS | Web Password Reset |  | Press and hold Enter to reset the web password to the factory default.
PAr | Pair L/L | - | Press and hold Enter until red LED blinks. (PAS) successful pairing. (FAi) pairing failed. Only two controllers can be present on network.
UnP | Unpair L/L | - | Press and hold Enter until red LED blinks. (PAS) successful unpairing. (FAi) unpairing failed.
bnd | Bond | - | Press and hold Enter until red LED blinks. (PAS) successful bonding. (FAi) bonding failed. Only two controllers can be present on network.
Unb | Unbond | - | Press and hold Enter until red LED blinks. (PAS) successful unbonding. (FAi) unbonding failed.
SA | Smart Access | Disabled | Turn KE2 Smart Access on or off. (EnA) Enable KE2 Smart Access. (diS) Disable KE2 Smart Access.
dHC | DHCP | Enabled | Turn DHCP mode on or off. (EnA) Enable DHCP mode. (diS) Disable DHCP mode.
Not Available on Basic Display | Motor Type | Bipolar | Type of motor on electric valve used
| Motor Step Rate | 200 | Motor step rate for EEV
| Max Valve Steps | 2500 | Full stroke steps for EEV
| Max Operating Press | 150 psig | Max operating pressure. Mas is 300 when R-410a is selected and 500 when R-744 is selected
| Fan Speed | 0% | Fan Speed %
| Min Comp Run Time | 2 min | Minimum Compressor Run Time.
| Min Comp Off Time | 5 min | Minimum Compressor Off Time.
| 1st Defrost Delay | 120 min | Delay time for first defrost when using scheduled defrost.
| Defrost Fan State | Off(E) On(A) | Off=Fans off during defrost; On=Fan on during defrost
| Fan Delay Temp | 5.0 F | Fan delay temp after defrost only.
| Max Fan Delay Time | 3 min | Max fan delay time after defrost.
| Pump Down Time | 0 min | Minimum time between de-energizing the liquid line solenoid/compressor contactor relay and energizing the defrost relay.
| Multi Air Temp CTRL | Warmest | Warmest air=use the warmest air temp from bonded controls; Average air= use the average air temp from bonded controls.
| Multi Evap Cool | Synchronized | Synchronized=synchronize bonded controllers in refrigeration mode; Independent= bonded controllers control temperature independently.
| Multi Evap Defrost | Synchronized | Synchronized=synchronized bonded controllers in defrost mode; Independent=bonded controllers defrost independently.
| Multi Evap Sensor | Shared | Shared=share sensor readings from bonded controllers; Unshared=use local sensor readings only.
| Room Temp Ind Def | 0.0 F | Room temp while bonded controller is in defrost. Only applies to bonded controllers with Multi Evap Defrost set to Independent.
| Suct Pres Offset | 0.0 F | Offset added or subtracted from the suction line pressure transducer reading, if needed.
| Suct Temp Offset | 0.0 F | Offset added or subtracted from the suction temp sensor reading, if needed.
| Coil Temp Offset | 0.0 F | Offset added or subtracted from the coil temperature sensor reading, if needed.
| Air Temp Offset | 0.0 F | offset added or subtracted from the room temperature sensor reading, if needed.
| Aux 1 Offset | 0.0 F | When Aux1, Aux2, or Aux3 is used as a temperature sensor an offset is added or subtracted from the reading.
| Aux 2 Offset | 0.0 F
| Aux 3 Offset | 0.0 F
| Proportional | 3 | Coefficient to valve control algorithm that increases valve responsiveness as the value increases.
| Intergral | 5 | Coefficient to valve control algorithm that increases valve responsiveness as the value increases.
| Derivative | 3 | Should not be adjusted unless instructed to by KE2 Therm
| Air Temp Diff | 1.0 F | Degrees above Room Temp before the controller will begin refrigeration